# SECTION 07 14 16

# COLD FLUID-APPLIED WATERPROOFING

# PART 1 GENERAL

## SECTION INCLUDES

### Cold liquid-applied elastomeric waterproofing membrane pitch extended polyurethane based on structural concrete for wet areas, basement, tunnels, inverted roofs, suspended slabs, balconies, and tanking systems.

## RELATED SECTIONS

### Section 03 30 00 – Cast-in-Place Concrete.

### Section 03 40 00 – Precast Concrete.

### Section 04 20 00 – Unit Masonry.

### Section 07 60 00 – Flashing and Sheet Metal.

### Section 07 92 00 – Joint Sealants.

### Section 07 92 13 – Elastomeric Joint Sealants.

### Section 33 46 13 – Foundation Drainage.

## REFERENCES

### ASTM – American Society for Testing and Materials

#### ASTM C717 – Standard Terminology of Building Seals and Sealants.

#### ASTM C794 – Standard Test Method for Adhesion-in-Peel of Elastomeric Joint Sealants.

#### ASTM C836 – Standard Specification for High Solids Content, Cold Liquid-Applied Elastomeric Waterproofing Membrane for Use with Separate Wearing Course.

#### ASTM C898 – Standard Guide for Use of High Solids Content, Cold Liquid-Applied Elastomeric Waterproofing Membrane with Separate Wearing Course

#### ASTM C1250 – Standard Test Method for Nonvolatile Content of Cold Liquid-Applied Elastomeric Waterproofing Membranes.

#### ASTM C1305 – Standard Test Method for Crack Bridging Ability of Liquid-Applied Waterproofing Membrane.

#### ASTM C1375 – Standard Guide for Substrates Used in Testing Building Seals and Sealants.

#### ASTM C1471 – Standard Guide for the Use of High Solids Content Cold Liquid-Applied Elastomeric Waterproofing Membrane on Vertical Surfaces.

#### ASTM C1522 – Standard Test Method for Extensibility After Heat Aging of Cold Liquid-Applied Elastomeric Waterproofing Membranes.

#### ASTM D2240 – Standard Test Method for Rubber Property-Durometer Hardness.

### EN – European Standard

#### EN 1062-3 - Paints and varnishes. Coating materials and coating systems for exterior masonry and concrete Determination of liquid water permeability.

#### EN 1062-6 - Paints and varnishes. Coating materials and coating systems for exterior masonry and concrete Determination of carbon dioxide permeability.

#### EN 1062-7 - Paints and varnishes. Coating materials and coating systems for exterior masonry and concrete Determination of crack bridging properties.

#### EN 1062-11 - Paints and varnishes. Coating materials and coating systems for exterior masonry and concrete Methods of conditioning before testing.

#### EN 1504-2 - Products and systems for the protection and repair of concrete structures - Definitions, requirements, quality control and evaluation of conformity - Part 2: Surface protection systems for concrete.

#### EN 1542 - Products and systems for the protection and repair of concrete structures - Test methods - Measurement of bond strength by pull-off.

#### EN 1770 - Products and systems for the protection and repair of concrete structures. Test methods. Determination of the coefficient of thermal expansion.

#### EN ISO 5470-1 - Rubber- or plastics-coated fabrics. Determination of abrasion resistance Taber abrader.

#### EN ISO 6272-1 - Paints and varnishes. Rapid-deformation (impact resistance) tests Falling-weight test, large-area indenter.

#### EN ISO 7783 - Paints and varnishes - Determination of water-vapor transmission properties - Cup method.

#### EN 13501-1 - Fire classification of construction products and building elements Classification using data from reaction to fire tests.

#### EN 13529 - Products and systems for the protection and repair of concrete structures. Test methods. Determination of resistance to severe chemical attack.

### SASO – The Saudi Standards, Metrology and Quality

#### SASO-EN-1504-2 - Products and systems for the protection and repair of concrete structures - Definitions, requirements, quality control and evaluation of conformity - Surface protection systems for concrete.

## DEFINITIONS

### Can’t-Strip: A beveled strip used under flashings to modify the angle at the point where the waterproofing membrane meets any vertical element.

### Elastomeric: A rubber like synthetic polymer that will stretch when pulled and will return quickly when released.

### Membrane: A flexible or semi-flexible waterproofing layer with the primary function of the exclusion of water.

### Reinforced Membrane: A waterproofing membrane reinforced with felts, mats, fabrics, or chopped fibers.

### Substrate: The surface upon which the waterproofing membrane is placed.

### Waterproofing: Treatment of a surface or structure to prevent the passage of water under hydrostatic pressure.

## SUBMITTALS

### The Contractor shall submit to the consultant, under the provisions of SECTION 013300, the following items for review and approval before commencing work:

#### Quality Control Program

##### The program shall cover items intended for shop inspection, field supervision and tests, as well as the procedures for carrying out the same, all-in accordance with SECTION 014500.

#### Product Data

##### Manufacturer’s catalogs, specifications, installation instructions, instructions for transporting, handling, and storing the materials and accessories to be used, and manufacturer’s quality control and quality assurance program related to the production, testing, and handling.

#### Certificates

##### Certificate of compliance stating that the materials used, and the installation procedures conform to all requirements of this Specification.

#### Samples

##### Samples shall be of 3 sets for all proposed materials.

#### Shop Drawings

##### Shop Drawings shall show all proposed work of this Section.

## QUALITY ASSURANCE

### Installer Qualifications: A firm that is approved by waterproofing manufacturer for installation of waterproofing required for this Project.

### Source Limitations: Obtain waterproofing materials and protection through one source from a single manufacturer to ensure compatibility. The source of each system component shall be confirmed.

### Pre-installation Conference: Conduct conference at Project site.

#### Review waterproofing requirements including surface preparation, substrate condition and pretreatment, minimum curing period, forecasted weather conditions, special details and installation procedures, testing and inspection procedures, protection, and repairs.

## HEALTH AND SAFETY CONSIDERTATIONS

### All works undertaken in relation to this Specification are to be completed in full accordance with the respective health and safety requirements established by the following:

#### United Arab Emirates

##### Legislation, Regulation, Standards and Codes.

#### Consultant Regulations

##### Standards, Contractual Conditions, and Health and Safety Systems.

#### Contractor

##### Health and Safety Standards and Systems as accepted by consultant.

### In the absence of any of the above, the best accepted industry practice shall be employed throughout.

## JOB CONDATIONS

### Waterproofing work shall be proceeded only after substrate construction and penetrating work have been completed.

### Weather Conditions

#### Installation shall be started when existing and forecasted weather conditions are within the limits established by the membrane manufacturer.

### Personnel shall be warned against breathing vapors and contact with skin and eyes.

### Keep flammable products away from sparks or flames. Spark producing equipment shall not be used during application and until vapors have dissipated.

### The work area shall be maintained in a neat and workable condition. Empty cartons and rubbish shall be removed from the site daily.

## WARRANTY

### The Contractor shall provide a written 10-years material warranty from the manufacturer, and 5-years for installation, upon completion and acceptance of the installation.

## PERFORMANCE REQUIREMENTS

### General

#### Provide a cold liquid-applied elastomeric waterproofing membrane polyurethane based that complies with physical requirements indicated in the approved product data.

## DELIVERY, HANDLING AND STORAGE

### The Contractor shall deliver, handle and store equipment and material units in accordance with SECTIONS 016500 and 016600, as well as the following requirements:

#### All materials shall be delivered to site in manufacturer’s original containers and pallets. Each container and pallet shall include a packing list in a waterproof envelope.

#### The materials shall be checked against packing lists on delivery to the work site and shall be inspected for damage. Damaged materials shall be removed from site.

#### Each container and individual roll of waterproofing kit shall be labeled to show brand name, type of material, lot and shelf life, date of manufacture, batch number and instructions for storage and handling, if any.

#### All materials shall be adequately protected during shipment, loading, and unloading, storage and installation against incidental damage, sunlight and ultraviolet radiation, rain, and high temperature.

#### The materials shall be stored in dry, shaded, and covered areas. In open areas, the materials shall be covered with a heavy-duty sheet. The kit of waterproofing shall be stored on a smooth hard surface.

#### All necessary precautions shall be taken to prevent fire hazards in the storage area and during installations.

# PART 2 PRODUCTS

## GENERAL

### All goods and products covered by these Specifications shall be procured, when available, from an in-Kingdom of Saudi Arabia manufacturer.

### Unless otherwise indicated, materials shall conform to the requirements specified herein.

## MATERIALS

### Cold liquid-applied elastomeric waterproofing membrane pitch extended polyurethane based: shall be two coats with total wet film thickness of 1.4 mm as approved by Engineer. The material should comply with ASTM C836, and meet the following physical properties:

#### Permeability: 0.035 H/m; ASTM E96.

#### Water vapor transmission: 9.6 gm/m² at 24 hours; ASTM E96.

#### Elongation: > 250 %; ASTM D412.

#### Tensile strength: 2 MPa; ASTM D412.

#### Elastic recovery: 95 %; ASTM D412.

#### Tear resistance: 10 KN/m; ASTM D624.

#### Shore A hardness: > 32; ASTM D2240.

#### Manufacturer:

##### Saudi Vetonit Co. Ltd. (SAVETO), Vetoproof UM766.

##### Or approved equal.

### Auxiliary Materials

#### General: Furnish auxiliary materials recommended by waterproofing manufacturer for intended use and compatible with waterproofing membrane.

#### Primer: Is not usually required on good concrete substrates; for highly porous or absorbent concrete shall be primed with a penetrating surface sealer water repellant.

#### Protection Board: Polypropylene (PP), or high-density polyethylene (HDPE) based.

# PART 3 EXECUTION

## EXAMINATION

### Surfaces and site conditions, under which waterproofing is to be performed, shall be verified, and examined if ready to receive work. Work shall not be started until all defects have been corrected.

#### Verify that substrates to receive waterproofing are clean, sound, smooth, free of fins and sharp edges, loose and foreign matter, oil and grease and anything detrimental to waterproofing membrane. Pitted surfaces must be repaired before membrane installation.

#### Notify the Engineer in writing of anticipated problems using waterproofing over substrate.

#### Proceed with installation only after unsatisfactory conditions have been corrected.

## SUBSTRATE PREPARATION

### General

#### Preparation of the surface shall be done in accordance with the waterproofing membrane manufacturer’s written instructions.

#### Surfaces shall be clean and smooth, free of depressions, waves, projections, voids, holes (tie rod or rock pockets), spatters, ridges, and loose aggregates. Any contaminants shall be removed such as grease, oil, and wax.

#### All sharp protrusion shall be ground smooth and all hollows and honeycomb voids, and similar surface defects shall be filled.

#### The surface shall be dry and shall be cleaned of all dust and debris.

#### Cracks shall be sealed using an approved sealant as recommended by the waterproofing manufacturer.

## PRIMING

### Prime porous surfaces with penetrating sealer water repellent and hardener primer by brush or roll and allow it to cure as per the manufacturer’s instructions.

## INSTALLATION

### Apply the first coat of waterproofing membrane with a brush or roll and allow it to cure as per the manufacturer’s instructions.

### Apply the second coat of waterproofing membrane with a brush or roll and allow it to cure as per the manufacturer’s instructions.

## CURING

### Allow the waterproofing to cure for at least 7 days or as per the manufacturer’s instructions, before commissioning or placing the protection board.

## PROTECTION AND CLEANING

### No storage of materials or traffic shall be allowed in unprotected areas with waterproofing material.

### Immediately following application, clean all tools and equipment with clean water. Hardened material can be removed by mechanical means.

### Remove leftover materials and any foreign material resulting from the work from the site.

# END OF SECTION